## R01
Determine Surge Protective Device (SPD) placement within facility. Complete Criteria Selections 1-7 below for each facility location (seven locations can be assessed on form). Total the value (refer to Table A for recommended SPD series/size). See Example Application below.
|  | Assessment Criteria Selection | [10 empty] | Location(s) | [6 empty] | Example Application
|  | 1. Electrical System Ampacity (at installation point) | [10 empty] | A | B | C | D | E | F | G
|  |  | 9 (2500-6000A) 7 (1200-2000A) 4 (600-1000A) | [16 empty] | 9 | 4,000A Switchgear
3 (225-400A) 2 (125-200A) 1 (Up to 100A)
SITE RISK ASSESSMENT |  | 2. Geographical Location (see Maps below) | [17 empty] | 3 | Dallas, TX 60 Storm Days
Proj Name |  |  | Isokeraunic Map (Thunderstorm Days/Year):
Proj Location |  |  | 4 (80-100) 3 (60-70) 2 (40-50) 1 (5-30)
Company |  |  | Mean Ground Flash Map (Mean Ground Flashes/Yr): | [16 empty] | 2 | 8 Flashes
Contact |  |  | 4 (13-16) 3 (9-12) 2 (5-8) 1 (1-4)
Ph | Fx | 3. System (AC) Voltage | [17 empty] | 3 | 480V
Email |  |  | 4 (600V) 3 (480V) 2 (240 or 208V) 1 (120V)
Prepared by |  | 4. Distribution System Configuration | [17 empty] | 3 | 3Æ WYE, 4W+G
Date |  |  | 3 (3Æ Wye 4W+G) 2 (3Æ Delta 3W+G) 1 (2Æ 3W+G)
|  | 5. Short Circuit Current (at installation point) | [17 empty] | 5 | 72kAIC
6 (101-200kA) 5 (51-100kA) 3 (26-50kA)
2 (15-25kA) 1 (5-14kA)
|  | 6. SPD Location (within electrical system) | [17 empty] | 8 | Svc Entrance w/Transfer Switch
8 (Svc Entrance w/Transfer Switch; power from utility)
7 (Svc Entrance w/o Transfer Switch; power from utility)
3 (Dist Panel >1000A; power from switchgear)
2 (Sub-dist Panel <1000A; power from panel; no Xfmr)
1 (Branch Panel <400A; power Xfmr)
|  | 7. Load Criticality Range: 3 (least) to 10 (most) | [17 empty] | 10 | 7x24 Data Ctr
|  | 8. Numerical Value Total (see Table A) | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 43 = TSr300
|  | Model Number (See Table C) | [13 empty] | Install Location - Description | [5 empty] | Qty
|  | Key |  | (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |  | (10)
|  | Example |  | TSr | i | 300 | F | x | 3Y4 | P | 2 | 01 |  | BFi |  | 4000A, 480/277Vac | [5 empty] | 1
A
B
C
D
E
F
G
[15 empty] | Table A | Recommended kA per Mode
[16 empty] | Numeric |  |  | Rating |  | Product
[16 empty] | Total |  |  | kA/Mode |  | Series
[16 empty] | 42 - 48 |  |  | 300kA |  | TSr300
[16 empty] | 35 - 41 |  |  | 250kA |  | TSr250
[16 empty] | 28 - 34 |  |  | 200kA |  | TSr200
[16 empty] | 21 - 27 |  |  | 150kA |  | TSr/TSn150
[16 empty] | 16 - 20 |  |  | 100kA |  | TSr/TSn100
[16 empty] | 11 - 15 |  |  | 50kA |  | TSr/TSn050
[15 empty] | Table B | OCPD Size per Thor SPD Series
Series TSr - 60A OCPD
Series TSn - 30A OCPD
[15 empty] | Table D | Ground Improvement Req'd?
[16 empty] | < 5 Ohms |  |  | Best |  | No
[16 empty] | 5-10 Ohms |  |  | Typical |  | No
[16 empty] | > 10 Ohms |  |  | High |  | Yes
THOR SYSTEMS, INC.
3621 Saunders Ave.
Richmond, VA 23227-4354
Ph 804/355-1100 Fx 804/355-8900
www.ThorSystems.us
(1) Thor Series
TSr Modular
TSn Non-Modular
Table C MODEL NUMBER
TSr i 300 F x 3Y4 P 2 01 BFi
Example Model #: TSri300Fx 3Y4 P201 BFi
Key (1) (2) (3) (4) (5) (6) (7) (8) (9) (10)
(2) Type *
i Industrial (w/ SADs)
c Commercial (w/o SADs)
* NOTE:
If Assessment #7, Load Criticality,
is 8 or higher, an Industrial Series is Recommended.
(3) Surge Current Rating
TSn or TSr TSr Only
050 ( 50kA/Mode) 200 (200kA/Mode)
100 (100ka/Mode) 250 (250kA/Mode)
150 (150kA/Mode) 300 (300kA/Mode)
(4) Input Connection Type
D Dist. Block (Up to 1/0AWG) [TSr Only]
F Fused Disconnect (Up to #6AWG [TSr Only)
T Terminal Block (Up to #4AWG) [TSr Only]
W Pre-Wired with #10AWG Wire [TSn Only]
(5) SAD Type
s 1.5kW Series
x 15kW Series
z No SAD's
(6) Voltage Configuration
2S1 (240/120V Single Phase, 3W+G) 3D2 (240V 3-Phase Delta, 3W+G)
2S2 (240V Single Phase, 2W+G) 3D4 (480V 3-Phase Delta, 3W+G)
2S4 (480V Single Phase, 2W+G) 3H_ (240V Hi-Leg Delta, 4W+G)
3Y2 (208/120V Three Phase, 4W+G) * 3R2 (208/120V H-Resis Gnd, 3W+G)
3Y4 (480/277V Three Phase, 4W+G) * 3R4 (480/277V H-Resis Gnd, 3W+G)
*SPD Built as Delta Configured - Neutral Conductor is not Connected
TSr Only
(9) Options
00 No Options
01 Form C
02 Extended EMi/RFi Filter
03 Phase Loss Contact
04 Multi-Function Relay
05 Combo of 01 & 02
06 Combo of 01 & 03
07 Combo of 01 & 04
08 Combo of 02 & 03
09 Combo of 03 & 04
10 Combo of 01, 02 & 03
11 Combo of 01, 03 & 04
TSr or TSn
(7) Enclosure Type
P Fiberglass, NEMA 4X [TSr Only]
Polycarbonate [TSn Only)
S Stainless Steel [TSr Only]
(8) Monitor Type
1 Status Lights Only
2 Status Lights, Surge Counter
& Audible Alarm
3 Status Lights & Audible
Alarm
(10) Orientation
TF Top Feed
TFi Top Feed, Internal Mounted Monitor
BF Bottom Feed
BFi Bottom Feed, Internal Mounted Monitor