## R01
Determine Surge Protective Device (SPD) placement within facility. Complete Criteria Selections 1-7 below for each facility location (seven locations can be assessed on form). Total the value (refer to Table B for recommended SPD series/size). See Example Application below.
|  | Assessment Criteria Selection | [10 empty] | Location(s) | [6 empty] | Example Application
|  | 1. Electrical System Capacity (at installation point) | [10 empty] | A | B | C | D | E | F | G
|  |  | 9 (2500-6000A) 7 (1200-2000A) 4 (600-1000A) | [16 empty] | 9 | 2,500A Switchgear
3 (225-400A) 2 (125-200A) 1 (Up to 100A)
SITE RISK ASSESSMENT |  | 2. Geographical Location (see Maps below) | [17 empty] | 3 | Dallas, TX 60 Storm Days
Proj Name |  |  | Isokeraunic Map (Thunderstorm Days/Year):
Proj Location |  |  | 4 (80-100) 3 (60-70) 2 (40-50) 1 (5-30)
Company |  |  | Mean Ground Flash Map (Mean Ground Flashes/Yr): | [16 empty] | 2 | 8 Flashes
Contact |  |  | 4 (13-16) 3 (9-12) 2 (5-8) 1 (1-4)
Ph | Fx | 3. System Voltage | [17 empty] | 3 | 480V
Email |  |  | 4 (600V) 3 (480V) 2 (240 or 208V) 1 (120V)
Prepared by |  | 4. Distribution System Configuration | [17 empty] | 3 | WYE
Date |  |  | 3 (WYE) 2 (Delta)(Hi-Res Gnd) 1 (Single Ph)
|  | 5. Short Circuit Current (at installation point) | [17 empty] | 5 | 65kAIC
6 (101-200kA) 5 (51-100kA) 3 (26-50kA)
2 (15-25kA) 1 (5-14kA)
|  | 6. SPD Location (within electrical system) | [17 empty] | 8 | Svc Entrance w/Transfer Switch
8 (Svc Entrance w/Transfer Switch; power from utility)
7 (Svc Entrance w/o Transfer Switch; power from utility)
3 (Dist Panel >1000A; power from switchgear)
2 (Sub-dist Panel <1000A; power from panel; no Xfmr)
1 (Branch Panel <400A; power Xfmr)
|  | 7. Load Criticality Range: 3 (least) to 10 (most) | [17 empty] | 10 | 7x24 Data Ctr
|  | 8. Numerical Value Total (see Table B) | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 43 = TSr300
|  | Model Number (See Table "A") | [13 empty] | Install Location - Description | [5 empty] | Qty
|  | Key |  | (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) |  | (10)
|  | Example |  | TSr | i | 300 | F | x | 3Y4 | P | 2 | 01 |  | BFi |  | MSB1; 2500A, 480/277Vac | [5 empty] | 1
A
B
C
D
E
F
G
Table "B" Numerical Total
Recm'd SPD kA/Mode
[16 empty] | Numeric |  |  | kA |  | Product
[16 empty] | Total |  |  | Rating |  | Series
[16 empty] | 42 - 48 |  |  | 300kA |  | TSr300
[16 empty] | 35 - 41 |  |  | 250kA |  | TSr250
[16 empty] | 28 - 34 |  |  | 200kA |  | TSr200
[16 empty] | 21 - 27 |  |  | 150kA |  | TSr/TSn150
[16 empty] | 16 - 20 |  |  | 100kA |  | TSr/TSn150
[16 empty] | 11 - 15 |  |  | 50kA |  | TSr/TSn150
Ground Improvement Required?
[16 empty] | < 5 Ohms |  |  | Best |  | No
[16 empty] | 5-10 Ohms |  |  | Typical |  | No
[16 empty] | > 10 Ohms |  |  | High |  | Yes
THOR SYSTEMS, INC.
3621 Saunders Ave.
Richmond, VA 23227-4354
Ph 804/355-1100 Fx 804/355-8900
www.ThorSystems.us